## REACTOR OL SETTING STG1
Northest Power Systems, Inc. - PAGE 1 | [5 empty] | Reactor Harmonic Current Spectrum - Page 3 | [11 empty] | current | time
66 Carey Road, Queensbury, NY 12804 Phone: 518-792-4776, Fax: 518-792-5767, Web: www.nepsi.com, Email: paul.steciuk@nepsi.com | [5 empty] | Harm # | (amps) | Harm # | (amps) | Harm # | (amps) | Harm # | (amps) |  |  |  |  | 39.4293 | 1000
BENSHAW INC. SPD SETTINGS SHEET - OVER LOAD RELAY - REACTOR | [17 empty] | 39.4293 | 30
SurProtex Digital Protection Relay | [5 empty] | I1 | 36.8602 | I11 | 0 | I21 | 0 | I31 | 0 | 1358.6731 | 0 | 0 | 0 | 70.9728 | 30.003
Branch Name: | [5 empty] | I2 | 0 | I12 | 0 | I22 | 0 | I32 | 0 | 0 | 0 | 0 | 0 | 70.9768 | 5
[6 empty] | I3 | 20 | I13 | 0 | I23 | 0 | I33 | 0 | 400 | 0 | 0 | 0 | 78.8587 | 4.9991
FILTER REACTOR FUNDAMENTAL CURRENT (AMPS): |  |  | 33.5093 | THIS VALUE IS BASED ON EFFECTIVE KVAR OUTPUT RATING OF FILTER BRANCH OR BANK |  | I4 | 0 | I14 | 0 | I24 | 0 | I34 | 0 | 0 | 0 | 0 | 0 | 78.9375 | 0.5
FILTER REACTOR FUNDAMENTAL CURRENT AT 10% OVER-VOLTAGE: |  |  | 36.8602 | FUNDAMENTAL CURRENT RATING OF BRANCH/BANK AT 10% OVER-VOLTAGE) |  | I5 | 0 | I15 | 0 | I25 | 0 | I35 | 0 | 0 | 0 | 0 | 0 | 236.5761 | 0.49999
FILTER REACTOR OVERLOAD SETTING LEVEL |  |  | 70% | TYPICALLY SET AT 70% OF THE REACTOR HARMONIC RSS RATING + THE FUNDAMENTAL CURRENT RATING OF THE BRANCH/BANK AT 10% OVER-VOLTAGE. |  | I6 | 0 | I16 | 0 | I26 | 0 | I36 | 0 | 0 | 0 | 0 | 0
FILTER REACTOR RECOMMENDED OVERLOAD SETTING |  |  | 39.4293 | THIS IS THE RECOMMENDED OVERLOAD RELAY SETTING PROVIDING 30% OF MARGIN FOR HARMONIC RATING. |  | I7 | 0 | I17 | 0 | I27 | 0 | I37 | 0 | 0 | 0 | 0 | 0
FILTER REACTOR MAXIMUM OVERLOAD SETTING |  |  | 41.9365 | THIS IS THE MAXIMUM OVERLOAD RELAY SETTING AND PROVIDES NO MARGIN. MONITOR EQUIPMENT IF THIS SETTING IS USED. |  | I8 | 0 | I18 | 0 | I28 | 0 | I38 | 0
[6 empty] | I9 | 0 | I19 | 0 | I29 | 0 | I39 | 0 | 0 | 0 | 0 | 0
When Setting Can be Made | Menu Item | SEL key - Available Settings | Recommended Setting | Description of Available Settings | Additional Notes | I10 | 0 | I20 | 0 | I30 | 0 | I40 | 0 | 0 | 0 | 0 | 0 | 39.4293 | 0.0001
[14 empty] | 0 | 0 | 0 | 0 | 39.4297 | 1000
These item may only be set in "test" mode | 1.CHA | Iinv/dEF | dEF | Inverse-time current curve/definite-time current curve | The definite time curve is recommended as a harmonic filter bank does not have a starting period. A definite time curve has a very predictable pick-up characteristic - same value of time for all amp values. | [8 empty] | 41.9365
| 2.dEF | 00-30 | 2 | Start Delay Time (sec) - delay period after initial startup of relay. | The definite time pickup noted in Menu Item 1.CHA above will not become active for 2 second after initial energization of relay. | Effective kvar rating of stage (kvar) |  |  | 800 | kvar |  |  |  | 20
| 3.r.P | oFF/on | oFF | Reverse phase detection | Reverse phase detection is disabled as it will not offer any additional protection for the harmonic filter. | System Voltage (kV) |  |  | 13.8 | kv
| 4.Und | OFF/30-70 | 70 | Undercurrent detection (% of current dial setting below). Or 27.6 amps based on the present dial setting. | A setting no greater than 93 should be used. A greater setting could cause nuisance trips. This setting will allow for the detection of blown fuses, etc.
| 5.Alt or g-F | oFF/60-110 | oFF | Alarm trip (%) | Not wired - therefore not set
| 6.StL | oFF/on | on | Long-time overcurrent trip | Feature is enabled to allow for long-time over-current trip. This function will cause a trip at 180% of the current dial setting or 71 amps at 5 seconds.
| 7.Loc | oFF/200-900 | 200 | Short-time overcurrent trip (% of current dail setting) | This setting is used for short-time over-current detection. Pickup occurs at this setting (in percent) multiplied by the current dial setting in 0.5 seconds or 78.9 amps
| 8.Ct | 1-120 | 10 | CT ratio. For example a 500/5 CT would have a setting of 100 | CT RATIO = 50/5
| 9.P-F | oFF/on | on | Phase failure detection | This protection feature is enabled to allow for the detection of a stuck vacuum switch or a main fuse operation.
| Sto | Sto | Sto | Hit the Store key to stall new values | The "Sto" key must be hit to store settings.
These settings can be made at any time | Time Dial | 00-63 | 30 | Trip time (seconds) | Allow up to 30 seconds before initiating a trip. This delay will allow motor starting, and other transient events to disapate befor initiating a filter trip.
| Current Dial | 5 to 63 amps | 39.4293 | Typically this setting is set below the RMS current rating of the filter component. | The current dial setting can be set whenever the relay is operation. The customer should be aware that touching this dial can result in a change of the over-current/over-load protection of the filter component.
Northest Power Systems, Inc. - Page 2
BENSHAW INC. SPD SETTINGS SHEET - OVER LOAD RELAY - REACTOR
When the SPD relay trips, the following Trip Indications will show on the display of the SPD relay. A reset must be performed to put the filter bank stage back into operation. Before resetting the relay, note the cause of the trip.
Display | Protection Function | Item Description
O-L | Thermal Overload | Filter Bank Reactor has exceeded its current dial setting of 39.4 amps. Reference Menu 1.CHA, 2.dEF, Current Dial setting, and Time Dial settings above. Increasing the Current Dial setting beyond the filter component rating should be done with extreme caution.
Und | Under Current | The filter bank drew less than the undercurrent setting for 3 seconds. Reference 4.Und above.
r-P | Reverse Phase | Line power phasing is reversed. This setting should not be used. NEPSI recomends this setting be disabled.
P-F | Phase Failure | One or more of the phases of the filter bank stage has been lost for more than 3 seconds. This trip could be caused by a main fuse operation or a stuck vacuum switch, if single phase vacuum switches are being used. Stuck open or stuck closed switches will result in this trip.
P-f | Phase Unbalance | One or more phases has been unbalanced by 50% for 5 seconds. Most likely cause of this trip will be a blown fuse condition.
StL | Long-time over-current trip | The filter bank drew more than 180% of the "current dial" setting for 5 seconds after being first energized.
Loc | Short-time over-current trip | The filter drew short-time high current for 0.5 Seconds. Reference the 7.Loc setting above.
g-F | Ground Fault | This function is not provided.
Bar Graph, 60-110% | Alarm Trip | Load is approaching the thermal limit. This function is not typically wire and is typically disabled. Reference 5.Alt above.

## RESISTOR OL SETTING
Northest Power Systems, Inc. - PAGE 1
66 Carey Road, Queensbury, NY 12804 Phone: 518-792-4776, Fax: 518-792-5767, Web: www.nepsi.com, Email: paul.steciuk@nepsi.com
BENSHAW INC. SPD SETTINGS SHEET - RESISTOR OVER LOAD RELAY' |  |  |  |  | RESISTOR KW/PHASE
SurProtex Digital Protection Relay |  |  |  |  | 30
Branch Name: | #VALUE! |  |  |  | RESISTOR OHMS/PHASE
100
FILTER RESISTOR CURRENT RATING (AMPS): |  |  | 17.3205 | TYPICALLY THIS WOULD BE THE RESISTOR RATING
FILTER RESISTOR OVERLOAD SETTING LEVEL |  |  | 70% | TYPICALLY SET AT 70% OF THE RESISTOR RATING.
FILTER RESISTOR RECOMMENDED OVERLOAD SETTING |  |  | 12.1244 | RECOMMENDED OVERLOAD RELAY TRIP SETTING WITH 30% OF MARGIN.
FILTER RESISTOR MAXIMUM RATING |  |  | 17.3205 | THIS IS THE MAXIMUM RSS VALUE OF THE RESISTOR
When Setting Can be Made | Menu Item | SEL key - Available Settings | Recommended Setting | Description of Available Settings | Additional Notes
These item may only be set in "test" mode | 1.CHA | Iinv/dEF | dEF | Inverse-time current curve/definite-time current curve | The definite time curve is recommended as a harmonic filter bank does not have a starting period. A definite time curve has a very predictable pick-up characteristic - same value of time for all amp values. | current | time
| 2.dEF | 00-30 | 5 | Start Delay Time (sec) - delay period after initial startup before over-load trip function becomes active. | The definite time pickup noted in Menu Item 1.CHA above will not become active for 5 second after initial current is sensed by the relay. | 12.1244 | 1000
| 3.r.P | oFF/on | oFF | Reverse phase detection | Reverse phase detection is disabled as it will not offer any additional protection for the harmonic filter. | 12.1244 | 30
| 4.Und | OFF/30-70 | oFF | Disabled | This is a under current trip setting. For high-pass filter resistors it is recommended to be set to OFF as the lack of harmonic current could result in a nuisance trip. | 21.8238 | 30.003
| 5.Alt or g-F | oFF/60-110 | oFF | Alarm trip (%) | Not wired - therefore not set | 21.8251 | 5
| 6.StL | oFF/on | on | Long-time overcurrent trip | Feature is enabled to allow for long-time over-current trip. This function will cause a trip at 180% of the current dial setting or 21.8 amps | 24.2487 | 4.9991
| 7.Loc | oFF/200-900 | 200 | Short-time overcurrent trip (% of current dail setting) | This setting is used for short-time over-current detection. Pickup occurs at this setting (in percent) multiplied by the current dial setting in 0.5 seconds or 24.2 amps | 24.273 | 0.5
| 8.Ct | 1-120 | 20 | CT ratio. For example a 500/5 CT would have a setting of 100 | CT RATIO = 100/5 | 72.7461 | 0.49999
| 9.P-F | oFF/on | on | Phase failure detection | This protection feature is enabled to allow for the detection of a stuck vacuum switch or a main fuse operation.
| Sto | Sto | Sto | Hit the Store key to stall new values | The "Sto" key must be hit to store settings.
These settings can be made at any time | Time Dial | 00-63 | 30 | Trip time (seconds) | Allow up to 30 seconds before initiating a trip. This delay will allow motor starting, and other transient events to disapate for initiating a trip. | 17.3205 | 0.0001
[6 empty] | 17.3207 | 1000
| Current Dial | 10 to 126 amps | 12.1244 | Typically this setting is set below the RMS current rating of the filter component. | The current dial setting can be set whenever the relay is operation. The customer should be aware that touching this dial can result in a change of the over-current/over-load protection of the filter component
Northest Power Systems, Inc. - PAGE 2
BENSHAW INC. SPD SETTINGS SHEET - RESISTOR OVER LOAD RELAY'
When the SPD relay trips, the following Trip Indications will show on the display of the SPD relay. A reset must be performed to put the filter bank stage back into operation. Before resetting the relay, note the cause of the trip.
Display | Protection Function | Item Description
O-L | Thermal Overload | Filter Bank has exceeded its current dial setting of 12.1 amps. Reference Menu 1.CHA, 2.dEF, Current Dial setting, and Time Dial settings above. Increasing the Current Dial setting beyond the filter component rating should be done with extreme caution.
Und | Under Current | The filter bank drew less than the undercurrent setting for 3 seconds. Reference 4.Und above.
r-P | Reverse Phase | Line power phasing is reversed. This setting should not be used. NEPSI recomends this setting be disabled.
P-F | Phase Failure | One or more of the phases of the filter bank stage has been lost for more than 3 seconds. This trip could be caused by a main fuse operation or a stuck vacuum switch, if single phase vacuum switches are being used. Stuck open or stuck closed switches will result in this trip.
P-f | Phase Unbalance | One or more phases has been unbalanced by 50% for 5 seconds. Most likely cause of this trip will be a blown fuse condition.
StL | Long-time over-current trip | The filter bank drew more than 180% of the "current dial" setting for 5 seconds after being first energized.
Loc | Short-time over-current trip | The filter drew short-time high current for 0.5 Seconds. Reference the 7.Loc setting above.
g-F | Ground Fault | This function is not provided.
Bar Graph, 60-110% | Alarm Trip | Load is approaching the thermal limit. This function is not typically wire and is typically disabled. Reference 5.Alt above.