## Out Rush Current Calculation
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY | [5 empty] | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
Learn more about outrush reactors with this YouTube Live Video.
CAPACITOR BANK OUT RUSH CURRENT CALCULATION | [6 empty] | https://youtu.be/YE-7cB8rG0U
Project Information
Customer Name: | Customer Name |  |  | Project Name: | Project Name
Equipment Tag: | Tag Name
Background Information
Formulas
Capacitor Bank & System Data
Incoming outrush reactor Inductance (µH) |  |  |  | 0 | (outrush reactor inductance on capacitor bank main or feeder cables)
Total inductance between capacitor bank and fault (µH) |  |  |  | 20 | (inductance of cables - assume 0.2 µH/Foot if not known)
Bank Voltage Rating (kV) |  | 25 |  | (a 10% over-voltage may be considered for worst case condition)
| Frequency Rating of Bank (HZ) | 60
| Stage Rating (kvar) | Stage Inrush/Outrush Inductance (µH) |  | Capacitance (µF) | Current Rating (amps)
Stage 1 | 10000 | 50 |  | 42.4426 | 231.2139 |  |  | 50 | 0.02
Stage 2 | 10000 | 50 |  | 42.4426 | 231.2139 |  |  | 50 | 0.02
Stage 3 | 10000 | 50 |  | 42.4426 | 231.2139 |  |  | 50 | 0.02
Stage 4 | 0 | 0 |  | 0 | 0 |  |  | 99999999999 | 1e-11
Stage 5 | 0 | 0 |  | 0 | 0 |  |  | 99999999999 | 1e-11
Stage 6 | 0 | 0 |  | 0 | 0 |  |  | 99999999999 | 1e-11
Stage 7 | 0 | 0 |  | 0 | 0 |  |  | 99999999999 | 1e-11
Stage 8 | 0 | 0 |  | 0 | 0 |  |  | 99999999999 | 1e-11
Leq (capacitor bank)(µH) | 16.6667 | Total Capacitance (µF) |  | 127.3277 |  |  |  |  | 0.06
Zo (total inductance)(µH) | 36.6667 | [7 empty] | 16.6667
Surge Impedance of Circuit (Zo) |  | 0.53663 | ohms
Peak Outrush Current (Io) |  | 38.0776 | kA (amps peak)
Outrush Frequency (f) |  | 2329.3554 | Hertz
I X f Product |  | 88.6962 | kAKHz
Angular Frequency (ωo) |  | 14635.3402 | rad/s
BREAKER RATING - Single Bank Operation
For C1 and C2 Rated Breakers
|  | Interrupt Rating (kA) |  | Close and Latch Rating | Within Close & Latch Rating
|  | 25 |  | 65 | Pass
Short Circuit Interrupt Rating (kA Sym) |  | 31.5 |  | 81.9 | Pass
|  | 40 |  | 104 | Pass
|  | 50 |  | 130 | Pass
|  | 63 |  | 163.8 | Pass
For General Purpose Breakers and C0 Rated Breakers
|  | Interrupt Rating (kA) |  | The lesser of 1.41 x Int Rating or 50 kA | Outrush Current Less than 20 kAKHz
|  | 25 |  | Fail | Fail
Short Circuit Interrupt Rating (kA Sym) |  | 31.5 |  | Pass | Fail
|  | 40 |  | Pass | Fail
|  | 50 |  | Pass | Fail
|  | 63 |  | Pass | Fail
BREAKER RATING - Parallel Bank Operation (2-Identical Systems in Parallel)
For C1 and C2 Rated Breakers
|  | Interrupt Rating (kA) |  | Close and Latch Rating | Within Close & Latch Rating
|  | 25 |  | 65 | Fail
Short Circuit Interrupt Rating (kA Sym) |  | 31.5 |  | 81.9 | Pass
|  | 40 |  | 104 | Pass
|  | 50 |  | 130 | Pass
|  | 63 |  | 163.8 | Pass
For General Purpose Breakers and C0 Rated Breakers
|  | Interrupt Rating (kA) |  | The lesser of 1.41 x Int Rating or 50 kA | Outrush Current Less than 20 kAKHz
|  | 25 |  | Fail | Fail
Short Circuit Interrupt Rating (kA Sym) |  | 31.5 |  | Fail | Fail
|  | 40 |  | Fail | Fail
|  | 50 |  | Fail | Fail
|  | 63 |  | Fail | Fail
Where
  I(t) = Instantaneous Current
  IO = Maximum Peak Current
  ωO = Angular frequency
X
X = Close in fault Capacitors discharge into fault (note grounding/type of fault matter)
This spreadsheet provides calculation assistance for calculating peak outrush current and frequency associated with a capacitor bank and nearby feeder circuit breaker that may close into a nearby fault (see figure to right). In such a scenario, depending on the grounding of the capacitor bank and the type of fault, the discharge current could exceed the breakers rating. The magnitude and frequency of the outrush current is dependent upon the total equivalent inductance between the capacitor bank and the fault, the capacitor bank rating, and the point on the voltage waveform where the breaker closes into the fault. This spreadsheet calculates the worst case current magnitude, assuming the fault occurs at peak voltage with no dampening due to resistance in the circuit. The spreadsheet allows for entry of inductance associated with transient inrush reactors, commonly put on each stage of the capacitor bank, inductance associated with an outrush reactor, commonly put in the incoming compartment of the capacitor bank or in series with the capacitor bank feeder cables supplying the capacitor bank, and the total inductance of the cable length and assocaited bus work between the capacitor bank and the close in feeder fault.
Note: For ungrounded banks, cable faults do not contribute to outrush current as these are line-to-ground faults and there is not a complete circuit for the out rush current to flow.
Information and formulas used in the spreadsheet were obtained from IEEE Standard 1036-2010 - Guide for the Application of Shunt Capacitors and IEEE PES technical report PES-TR16 - Transient Limiting Inductor Applications in Shunt Capacitor Banks.
(amps)
𝑖(𝑡)=𝑉_max⁡(𝑃𝐸𝐴𝐾) /𝑍_𝑜 𝑆𝑖𝑛(𝜔_𝑜 𝑡) (amps)
(amps peak)
𝐼_𝑜=𝑉_max⁡(𝑃𝐸𝐴𝐾) /𝑍_𝑜 (amps peak)
(ohms)
𝑍_𝑜=√(𝐿_𝑠/𝐶_𝑡𝑜𝑡𝑎𝑙 ) (ohms)
(rad/s)
𝜔_𝑜=2𝜋𝑓=√(1/〖𝐶_𝑡𝑜𝑡𝑎𝑙 𝐿〗_𝑆 ) (rad/s)
  LS = Total inductance to fault
  Vmax(peak) = Maximum peak line-to-neutral voltage
  Ctotal = Total phase capacitance of capacitor bank
  ZO = Surge Impedance of circuit
Internal Inductance associated with the capacitor bank itself or internal bus work.
IEEE Std. C37.012-2005 - Application Guide for Capacitance Current Switching for AC High-Voltage Circuit Breakers provides the following basic approximatations for capacitor bank inductance :
Bus work between stages:
17.5kV and Below: 0.23uH/foot 38kV and below: 0.26uH/foot
Internal Inductance of capacitor stage:
Inductance/stages: 5uH/Stage - This does not included any added inductance associated with back-to-back inrush reactors placed on each stage.
Add above values to inrush reactors.
𝐿_𝑒𝑞=1/(1/𝐿_1 +1/𝐿_2 +1/𝐿_3 +⋯1/𝐿_𝑛 )
𝐿_𝑆=𝐿_𝑒𝑞+𝐿_𝑜𝑢𝑡𝑟𝑢𝑠ℎ+𝐿_(𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑜𝑟−𝑡𝑜−𝑓𝑎𝑢𝑙𝑡)

## C37.06 - 2009
Note Paragraph to left for general purpose breakers.
Note current inrush peak and frequency may break from preferred standard values.
Note Paragraph to left for C1 and C2 rated breakers. (The peak withstand and close & latch rating = 2.6 x breaker sym. short circuit rating)